
Restore Factory Parameters (PP.01=1)
Check if the Wiring is Correct
Start of Vector Control Terminal Mode Commissioning

P1-00= Motor Type


Change Control Mode
P1-01= Motor power

PO.01=0 (Open - loop Vector Control)
P1.02= Motor voltage



P1.03= Motor current



Input Motor Nameplate Parameters
P1.04= Motor frequency



P1.05= Motor speed




Motor Parameter Input Completed


P1.37=1 Static Tuning for Asynchronous Motor
P1.37=11 Static Tuning for Synchronous Motor

Troubleshoot according to fault codes; contact the manufacturer if unresolved

If a fault is reported

Tuning steps

根据故障代码排除，无法解决时请联系厂家

Start motor tuning

开始电机调谐

Press the Confirm Key; the Operation Panel Displays ARUN and Flashes. Then Press the RUN Key; the Drive Enters Tuning State. (After Tuning is Completed, the Drive Operation Panel Automatically Returns to Parameter Display State)


Tuning completed
调谐完成

If the rotation direction is incorrect



Modify Parameter P0.9=0/1 or After Power - off, Swap Any Two Motor Wires, then Power on and Retune (Retuning is Mandatory; Direct Operation is Not Allowed)
Check if the motor rotation direction is correct
看电机转向是否正确



Method

1. Modify Command Source Parameter P0.02=1, Select Command Source (Terminal Command)
2.Modify Main Frequency Source Parameter P0.03=(2 Corresponding to AI1), (3 Corresponding to AI2), (4 Corresponding to AI3)
Rotation direction correct
Adjust the Panel Potentiometer to Set the Frequency to 2, Press the Run Key, and Check if the Motor Rotation Direction is Correct

